## drive_ratings
family | supply_v | mounting | duty | kw | hp | reference | line_current_a | line_current_b | max_continuous_a | max_transient_60s_a | has_dc_choke | emc_note | ip_note | variant_rank | is_default_variant | source_pdf | source_page
ATV630 | 200-240 V | wall | ND | 0.75 | 1 | ATV630U07M3 | 3 | 2.6 | 4.6 | 5.1 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 200-240 V | wall | HD | 0.37 | 0.5 | ATV630U07M3 | 1.7 | 1.5 | 3.3 | 5 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 200-240 V | wall | ND | 1.5 | 2 | ATV630U15M3 | 5.9 | 5 | 8 | 8.8 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 200-240 V | wall | HD | 0.75 | 1 | ATV630U15M3 | 3.3 | 3 | 4.6 | 6.9 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 200-240 V | wall | ND | 2.2 | 3 | ATV630U22M3 | 8.4 | 7.2 | 11.2 | 12.3 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 200-240 V | wall | HD | 1.5 | 2 | ATV630U22M3 | 6 | 5.3 | 8 | 12 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 200-240 V | wall | ND | 3 |  | ATV630U30M3 | 11.5 | 9.9 | 13.7 | 15.1 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 200-240 V | wall | HD | 2.2 | 3 | ATV630U30M3 | 8.7 | 7.6 | 11.2 | 16.8 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 200-240 V | wall | ND | 4 | 5 | ATV630U40M3 | 15.1 | 12.9 | 18.7 | 20.6 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 200-240 V | wall | HD | 3 |  | ATV630U40M3 | 11.7 | 10.2 | 13.7 | 20.6 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 200-240 V | wall | ND | 5.5 | 7.5 | ATV630U55M3 | 20.2 | 17.1 | 25.4 | 27.9 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 200-240 V | wall | HD | 4 | 5 | ATV630U55M3 | 15.1 | 13 | 18.7 | 28.1 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 200-240 V | wall | ND | 7.5 | 10 | ATV630U75M3 | 27.1 | 22.8 | 32.7 | 36 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 200-240 V | wall | HD | 5.5 | 7.5 | ATV630U75M3 | 20.2 | 17.1 | 25.4 | 38.1 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 200-240 V | wall | ND | 11 | 15 | ATV630D11M3 | 39.3 | 32.9 | 46.8 | 51.5 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 200-240 V | wall | HD | 7.5 | 10 | ATV630D11M3 | 27.2 | 23.1 | 32.7 | 49.1 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 200-240 V | wall | ND | 15 | 20 | ATV630D15M3 | 52.6 | 45.5 | 63.4 | 69.7 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 200-240 V | wall | HD | 11 | 15 | ATV630D15M3 | 40.1 | 34.3 | 46.8 | 70.2 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 200-240 V | wall | ND | 18.5 | 25 | ATV630D18M3 | 66.7 | 54.5 | 78.4 | 86.2 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 200-240 V | wall | HD | 15 | 20 | ATV630D18M3 | 53.1 | 44.9 | 63.4 | 95.1 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 200-240 V | wall | ND | 22 | 30 | ATV630D22M3 | 76 | 64.3 | 92.6 | 101.9 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 200-240 V | wall | HD | 18.5 | 25 | ATV630D22M3 | 64.8 | 54.5 | 78.4 | 117.6 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 200-240 V | wall | ND | 30 | 40 | ATV630D30M3 | 104.7 | 88.6 | 123 | 135.3 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 200-240 V | wall | HD | 22 | 30 | ATV630D30M3 | 78.3 | 67.1 | 92.6 | 138.9 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 200-240 V | wall | ND | 37 | 50 | ATV630D37M3 | 128 | 107.8 | 149 | 163.9 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 200-240 V | wall | HD | 30 | 40 | ATV630D37M3 | 104.7 | 88.6 | 123 | 184.5 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 200-240 V | wall | ND | 45 | 60 | ATV630D45M3 | 155.1 | 130.4 | 176 | 193.6 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 200-240 V | wall | HD | 37 | 50 | ATV630D45M3 | 128.5 | 108.5 | 149 | 223.5 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 200-240 V | wall | ND | 55 | 75 | ATV630D55M3 | 189 | 161 | 211 | 232.1 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 200-240 V | wall | HD | 45 | 60 | ATV630D55M3 | 156 | 134 | 176 | 264 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 200-240 V | wall | ND | 75 | 100 | ATV630D75M3 | 256 | 215 | 282 | 310.2 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 200-240 V | wall | HD | 55 | 75 | ATV630D75M3 | 189 | 161 | 211 | 316.5 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 24
ATV630 | 380-480 V | wall | ND | 0.75 | 1 | ATV630U07N4 | 1.5 | 1.3 | 2.2 | 2.4 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 25
ATV630 | 380-480 V | wall | HD | 0.37 | 0.5 | ATV630U07N4 | 0.9 | 0.8 | 1.5 | 2.3 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 25
ATV630 | 380-480 V | wall | ND | 1.5 | 2 | ATV630U15N4 | 3 | 2.6 | 4 | 4.4 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 25
ATV630 | 380-480 V | wall | HD | 0.75 | 1 | ATV630U15N4 | 1.7 | 1.5 | 2.2 | 3.3 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 25
ATV630 | 380-480 V | wall | ND | 2.2 | 3 | ATV630U22N4 | 4.3 | 3.8 | 5.6 | 6.2 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 25
ATV630 | 380-480 V | wall | HD | 1.5 | 2 | ATV630U22N4 | 3.1 | 2.9 | 4 | 6 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 25
ATV630 | 380-480 V | wall | ND | 3 |  | ATV630U30N4 | 5.8 | 5.1 | 7.2 | 7.9 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 25
ATV630 | 380-480 V | wall | HD | 2.2 | 3 | ATV630U30N4 | 4.5 | 4 | 5.6 | 8.4 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 25
ATV630 | 380-480 V | wall | ND | 4 | 5 | ATV630U40N4 | 7.6 | 6.7 | 9.3 | 10.2 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 25
ATV630 | 380-480 V | wall | HD | 3 |  | ATV630U40N4 | 6 | 5.4 | 7.2 | 10.8 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 25
ATV630 | 380-480 V | wall | ND | 5.5 | 7.5 | ATV630U55N4 | 10.4 | 9.1 | 12.7 | 14 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 25
ATV630 | 380-480 V | wall | HD | 4 | 5 | ATV630U55N4 | 8 | 7.2 | 9.3 | 14 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 25
ATV630 | 380-480 V | wall | ND | 7.5 | 10 | ATV630U75N4 | 13.8 | 11.9 | 16.5 | 18.2 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 25
ATV630 | 380-480 V | wall | HD | 5.5 | 7.5 | ATV630U75N4 | 10.5 | 9.2 | 12.7 | 19.1 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 25
ATV630 | 380-480 V | wall | ND | 11 | 15 | ATV630D11N4 | 19.8 | 17 | 23.5 | 25.9 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 25
ATV630 | 380-480 V | wall | HD | 7.5 | 10 | ATV630D11N4 | 14.1 | 12.5 | 16.5 | 24.8 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 25
ATV630 | 380-480 V | wall | ND | 15 | 20 | ATV630D15N4 | 27 | 23.3 | 31.7 | 34.9 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 25
ATV630 | 380-480 V | wall | HD | 11 | 15 | ATV630D15N4 | 20.6 | 18.1 | 23.5 | 35.3 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 25
ATV630 | 380-480 V | wall | ND | 18.5 | 25 | ATV630D18N4 | 33.4 | 28.9 | 39.2 | 43.1 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 25
ATV630 | 380-480 V | wall | HD | 15 | 20 | ATV630D18N4 | 27.7 | 24.4 | 31.7 | 47.6 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 25
ATV630 | 380-480 V | wall | ND | 22 | 30 | ATV630D22N4 | 39.6 | 34.4 | 46.3 | 50.9 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 25
ATV630 | 380-480 V | wall | HD | 18.5 | 25 | ATV630D22N4 | 34.1 | 29.9 | 39.2 | 58.8 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 25
ATV630 | 380-480 V | wall | ND | 30 | 40 | ATV630D30N4 | 53.3 | 45.9 | 61.5 | 67.7 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 25
ATV630 | 380-480 V | wall | HD | 22 | 30 | ATV630D30N4 | 40.5 | 35.8 | 46.3 | 69.5 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 25
ATV630 | 380-480 V | wall | ND | 37 | 50 | ATV630D37N4 | 66.2 | 57.3 | 74.5 | 82 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 25
ATV630 | 380-480 V | wall | HD | 30 | 40 | ATV630D37N4 | 54.8 | 48.3 | 61.5 | 92.3 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 25
ATV630 | 380-480 V | wall | ND | 45 | 60 | ATV630D45N4 | 79.8 | 69.1 | 88 | 96.8 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 25
ATV630 | 380-480 V | wall | HD | 37 | 50 | ATV630D45N4 | 67.1 | 59 | 74.5 | 111.8 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 25
ATV630 | 380-480 V | wall | ND | 55 | 75 | ATV630D55N4 | 97.2 | 84.2 | 106 | 116.6 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 26
ATV630 | 380-480 V | wall | HD | 45 | 60 | ATV630D55N4 | 81.4 | 71.8 | 88 | 132 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 26
ATV630 | 380-480 V | wall | ND | 75 | 100 | ATV630D75N4 | 131.3 | 112.7 | 145 | 159.5 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 26
ATV630 | 380-480 V | wall | HD | 55 | 75 | ATV630D75N4 | 98.9 | 86.9 | 106 | 159 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 26
ATV630 | 380-480 V | wall | ND | 90 | 125 | ATV630D90N4 | 156.2 | 135.8 | 173 | 190.3 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 26
ATV630 | 380-480 V | wall | HD | 75 | 100 | ATV630D90N4 | 134.3 | 118.1 | 145 | 217.5 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 26
ATV630 | 380-480 V | wall | ND | 110 | 150 | ATV630C11N4 | 201 | 165 | 211 | 232.1 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 26
ATV630 | 380-480 V | wall | HD | 90 | 125 | ATV630C11N4 | 170 | 143 | 173 | 259.5 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 26
ATV630 | 380-480 V | wall | ND | 132 | 200 | ATV630C13N4 | 237 | 213 | 250 | 275 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 26
ATV630 | 380-480 V | wall | HD | 110 | 150 | ATV630C13N4 | 201 | 165 | 211 | 317 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 26
ATV630 | 380-480 V | wall | ND | 160 | 250 | ATV630C16N4 | 284 | 262 | 302 | 332.2 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 26
ATV630 | 380-480 V | wall | HD | 132 | 200 | ATV630C16N4 | 237 | 213 | 250 | 375 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 26
ATV630 | 380-480 V | wall | ND | 220 | 350 | ATV630C22N4 | 397 | 324 | 427 | 470 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 26
ATV630 | 380-480 V | wall | HD | 160 | 250 | ATV630C22N4 | 296 | 246 | 302 | 453 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 26
ATV630 | 380-480 V | wall | ND | 250 | 400 | ATV630C25N4 | 451 | 366 | 481 | 529 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 26
ATV630 | 380-480 V | wall | HD | 220 | 300 | ATV630C25N4 | 365 | 301 | 387 | 581 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 26
ATV630 | 380-480 V | wall | ND | 315 | 500 | ATV630C31N4 | 569 | 461 | 616 | 678 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 26
ATV630 | 380-480 V | wall | HD | 250 | 400 | ATV630C31N4 | 457 | 375 | 481 | 722 | true |  | IP21 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 26
ATV650 | 380-480 V | wall | ND | 0.75 | 1 | ATV650U07N4 | 1.5 | 1.3 | 2.2 | 2.4 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | HD | 0.37 | 0.5 | ATV650U07N4 | 0.9 | 0.8 | 1.5 | 2.3 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | ND | 1.5 | 2 | ATV650U15N4 | 3 | 2.6 | 4 | 4.4 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | HD | 0.75 | 1 | ATV650U15N4 | 1.7 | 1.5 | 2.2 | 3.3 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | ND | 2.2 | 3 | ATV650U22N4 | 4.3 | 3.8 | 5.6 | 6.2 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | HD | 1.5 | 2 | ATV650U22N4 | 3.1 | 2.9 | 4 | 6 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | ND | 3 |  | ATV650U30N4 | 5.8 | 5.1 | 7.2 | 7.9 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | HD | 2.2 | 3 | ATV650U30N4 | 4.5 | 4 | 5.6 | 8.4 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | ND | 4 | 5 | ATV650U40N4 | 7.6 | 6.7 | 9.3 | 10.2 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | HD | 3 |  | ATV650U40N4 | 6 | 5.4 | 7.2 | 10.8 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | ND | 5.5 | 7.5 | ATV650U55N4 | 10.4 | 9.1 | 12.7 | 14 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | HD | 4 | 5 | ATV650U55N4 | 8 | 7.2 | 9.3 | 14 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | ND | 7.5 | 10 | ATV650U75N4 | 13.8 | 11.9 | 16.5 | 18.2 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | HD | 5.5 | 7.5 | ATV650U75N4 | 10.5 | 9.2 | 12.7 | 19.1 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | ND | 11 | 15 | ATV650D11N4 | 19.8 | 17 | 23.5 | 25.9 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | HD | 7.5 | 10 | ATV650D11N4 | 14.1 | 12.5 | 16.5 | 24.8 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | ND | 15 | 20 | ATV650D15N4 | 27 | 23.3 | 31.7 | 34.9 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | HD | 11 | 15 | ATV650D15N4 | 20.6 | 18.1 | 23.5 | 35.3 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | ND | 18.5 | 25 | ATV650D18N4 | 33.4 | 28.9 | 39.2 | 43.1 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | HD | 15 | 20 | ATV650D18N4 | 27.7 | 24.4 | 31.7 | 47.6 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | ND | 22 | 30 | ATV650D22N4 | 39.6 | 34.4 | 46.3 | 50.9 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | HD | 18.5 | 25 | ATV650D22N4 | 34.1 | 29.9 | 39.2 | 58.8 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | ND | 30 | 40 | ATV650D30N4 | 53.3 | 45.9 | 61.5 | 67.7 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | HD | 22 | 30 | ATV650D30N4 | 40.5 | 35.8 | 46.3 | 69.5 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | ND | 37 | 50 | ATV650D37N4 | 66.2 | 57.3 | 74.5 | 82 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | HD | 30 | 40 | ATV650D37N4 | 54.8 | 48.3 | 61.5 | 92.3 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | ND | 45 | 60 | ATV650D45N4 | 79.8 | 69.1 | 88 | 96.8 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | HD | 37 | 50 | ATV650D45N4 | 67.1 | 59 | 74.5 | 111.8 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | ND | 55 | 75 | ATV650D55N4 | 97.2 | 84.2 | 106 | 116.6 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | HD | 45 | 60 | ATV650D55N4 | 81.4 | 71.8 | 88 | 132 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | ND | 75 | 100 | ATV650D75N4 | 131.3 | 112.7 | 145 | 159.5 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | HD | 55 | 75 | ATV650D75N4 | 98.9 | 86.9 | 106 | 159 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | ND | 90 | 125 | ATV650D90N4 | 156.2 | 135.8 | 173 | 190.3 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | HD | 75 | 100 | ATV650D90N4 | 134.3 | 118.1 | 145 | 217.5 | true | C2 | IP55 | 10 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 27
ATV650 | 380-480 V | wall | ND | 0.75 | 1 | ATV650U07N4E | 1.5 | 1.3 | 2.2 | 2.4 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | HD | 0.37 | 0.5 | ATV650U07N4E | 0.9 | 0.8 | 1.5 | 2.3 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | ND | 1.5 | 2 | ATV650U15N4E | 3 | 2.6 | 4 | 4.4 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | HD | 0.75 | 1 | ATV650U15N4E | 1.7 | 1.5 | 2.2 | 3.3 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | ND | 2.2 | 3 | ATV650U22N4E | 4.3 | 3.8 | 5.6 | 6.2 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | HD | 1.5 | 2 | ATV650U22N4E | 3.1 | 2.9 | 4 | 6 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | ND | 3 |  | ATV650U30N4E | 5.8 | 5.1 | 7.2 | 7.9 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | HD | 2.2 | 3 | ATV650U30N4E | 4.5 | 4 | 5.6 | 8.4 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | ND | 4 | 5 | ATV650U40N4E | 7.6 | 6.7 | 9.3 | 10.2 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | HD | 3 |  | ATV650U40N4E | 6 | 5.4 | 7.2 | 10.8 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | ND | 5.5 | 7.5 | ATV650U55N4E | 10.4 | 9.1 | 12.7 | 14 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | HD | 4 | 5 | ATV650U55N4E | 8 | 7.2 | 9.3 | 14 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | ND | 7.5 | 10 | ATV650U75N4E | 13.8 | 11.9 | 16.5 | 18.2 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | HD | 5.5 | 7.5 | ATV650U75N4E | 10.5 | 9.2 | 12.7 | 19.1 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | ND | 11 | 15 | ATV650D11N4E | 19.8 | 17 | 23.5 | 25.9 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | HD | 7.5 | 10 | ATV650D11N4E | 14.1 | 12.5 | 16.5 | 24.8 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | ND | 15 | 20 | ATV650D15N4E | 27 | 23.3 | 31.7 | 34.9 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | HD | 11 | 15 | ATV650D15N4E | 20.6 | 18.1 | 23.5 | 35.3 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | ND | 18.5 | 25 | ATV650D18N4E | 33.4 | 28.9 | 39.2 | 43.1 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | HD | 15 | 20 | ATV650D18N4E | 27.7 | 24.4 | 31.7 | 47.6 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | ND | 22 | 30 | ATV650D22N4E | 39.6 | 34.4 | 46.3 | 50.9 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | HD | 18.5 | 25 | ATV650D22N4E | 34.1 | 29.9 | 39.2 | 58.8 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | ND | 30 | 40 | ATV650D30N4E | 53.3 | 45.9 | 61.5 | 67.7 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | HD | 22 | 30 | ATV650D30N4E | 40.5 | 35.8 | 46.3 | 69.5 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | ND | 37 | 50 | ATV650D37N4E | 66.2 | 57.3 | 74.5 | 82 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | HD | 30 | 40 | ATV650D37N4E | 54.8 | 48.3 | 61.5 | 92.3 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | ND | 45 | 60 | ATV650D45N4E | 79.8 | 69.1 | 88 | 96.8 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | HD | 37 | 50 | ATV650D45N4E | 67.1 | 59 | 74.5 | 111.8 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | ND | 55 | 75 | ATV650D55N4E | 97.2 | 84.2 | 106 | 116.6 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | HD | 45 | 60 | ATV650D55N4E | 81.4 | 71.8 | 88 | 132 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | ND | 75 | 100 | ATV650D75N4E | 131.3 | 112.7 | 145 | 159.5 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | HD | 55 | 75 | ATV650D75N4E | 98.9 | 86.9 | 106 | 159 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | ND | 90 | 125 | ATV650D90N4E | 156.2 | 135.8 | 173 | 190.3 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV650 | 380-480 V | wall | HD | 75 | 100 | ATV650D90N4E | 134.3 | 118.1 | 145 | 217.5 | true | C2 | IP55 | 20 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 28
ATV630 | 500-690 V | wall | ND | 1.5 | 2 | ATV630U22Y6 | 3.4 | 3.6 | 3.1 | 3.4 | unknown |  | IP00 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 29
ATV630 | 500-690 V | wall | HD | 1.1 | 1.5 | ATV630U22Y6 | 2.6 | 2.6 | 2.4 | 3.6 | unknown |  | IP00 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 29
ATV630 | 500-690 V | wall | ND | 2.2 | 3 | ATV630U30Y6 | 4.7 | 4.8 | 4.2 | 4.6 | unknown |  | IP00 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 29
ATV630 | 500-690 V | wall | HD | 1.5 | 2 | ATV630U30Y6 | 3.4 | 3.6 | 3.1 | 4.7 | unknown |  | IP00 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 29
ATV630 | 500-690 V | wall | ND | 3 |  | ATV630U40Y6 | 6.2 | 6.1 | 5.4 | 5.9 | unknown |  | IP00 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 29
ATV630 | 500-690 V | wall | HD | 2.2 | 3 | ATV630U40Y6 | 4.7 | 4.8 | 4.2 | 6.3 | unknown |  | IP00 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 29
ATV630 | 500-690 V | wall | ND | 4 | 5 | ATV630U55Y6 | 7.9 | 8 | 7.2 | 7.9 | unknown |  | IP00 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 29
ATV630 | 500-690 V | wall | HD | 3 |  | ATV630U55Y6 | 6.2 | 6.1 | 5.4 | 8.1 | unknown |  | IP00 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 29
ATV630 | 500-690 V | wall | ND | 5.5 | 7.5 | ATV630U75Y6 | 10.4 | 10.5 | 9.5 | 10.5 | unknown |  | IP00 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 29
ATV630 | 500-690 V | wall | HD | 4 | 5 | ATV630U75Y6 | 7.9 | 8 | 7.2 | 10.8 | unknown |  | IP00 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 29
ATV630 | 500-690 V | wall | ND | 7.5 | 10 | ATV630D11Y6 | 13.6 | 14.7 | 13.5 | 14.9 | unknown |  | IP00 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 29
ATV630 | 500-690 V | wall | HD | 5.5 | 7.5 | ATV630D11Y6 | 10.4 | 10.5 | 9.5 | 14.3 | unknown |  | IP00 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 29
ATV630 | 500-690 V | wall | ND | 11 | 15 | ATV630D15Y6 | 18.4 | 19.2 | 18 | 19.8 | unknown |  | IP00 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 29
ATV630 | 500-690 V | wall | HD | 7.5 | 10 | ATV630D15Y6 | 13.6 | 14.7 | 13.5 | 20.3 | unknown |  | IP00 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 29
ATV630 | 500-690 V | wall | ND | 15 | 20 | ATV630D18Y6 | 23.1 | 23 | 24 | 26.4 | unknown |  | IP00 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 29
ATV630 | 500-690 V | wall | HD | 11 | 15 | ATV630D18Y6 | 18.4 | 19.2 | 18 | 27 | unknown |  | IP00 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 29
ATV630 | 500-690 V | wall | ND | 18.5 | 25 | ATV630D22Y6 | 27.6 | 26 | 29 | 31.9 | unknown |  | IP00 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 29
ATV630 | 500-690 V | wall | HD | 15 | 20 | ATV630D22Y6 | 23.2 | 23 | 24 | 36 | unknown |  | IP00 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 29
ATV630 | 500-690 V | wall | ND | 22 | 30 | ATV630D30Y6 | 32.1 | 32.8 | 34 | 37.4 | unknown |  | IP00 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 29
ATV630 | 500-690 V | wall | HD | 18.5 | 25 | ATV630D30Y6 | 27.6 | 26 | 29 | 43.5 | unknown |  | IP00 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 29
ATV630 | 500-690 V | wall | ND | 30 | 40 | ATV630D37Y6 | 47.2 | 46.2 | 45 | 49.5 | unknown |  | IP00 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 29
ATV630 | 500-690 V | wall | HD | 22 | 30 | ATV630D37Y6 | 37.7 | 38.5 | 34 | 51 | unknown |  | IP00 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 29
ATV630 | 500-690 V | wall | ND | 37 | 50 | ATV630D45Y6 | 55.6 | 54.4 | 55 | 60.5 | unknown |  | IP00 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 29
ATV630 | 500-690 V | wall | HD | 30 | 40 | ATV630D45Y6 | 47.2 | 46.2 | 45 | 67.5 | unknown |  | IP00 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 29
ATV630 | 500-690 V | wall | ND | 45 | 60 | ATV630D55Y6 | 65.5 | 62.5 | 66 | 72.6 | unknown |  | IP00 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 29
ATV630 | 500-690 V | wall | HD | 37 | 50 | ATV630D55Y6 | 55.6 | 54.4 | 55 | 82.5 | unknown |  | IP00 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 29
ATV630 | 500-690 V | wall | ND | 55 | 75 | ATV630D75Y6 | 82.7 | 87.7 | 83 | 91.3 | unknown |  | IP00 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 29
ATV630 | 500-690 V | wall | HD | 45 | 60 | ATV630D75Y6 | 71 | 68.5 | 66 | 99 | unknown |  | IP00 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 29
ATV630 | 500-690 V | wall | ND | 75 | 100 | ATV630D90Y6 | 108.3 | 99.4 | 108 | 118.8 | unknown |  | IP00 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 29
ATV630 | 500-690 V | wall | HD | 55 | 75 | ATV630D90Y6 | 82.7 | 87.7 | 83 | 124.5 | unknown |  | IP00 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 29
ATV630 | 380-440 V | floor | ND | 110 |  | ATV630C11N4F | 207 | 195 | 211 | 232 | true | C3 | IP21 | 15 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 30
ATV630 | 380-440 V | floor | HD | 90 |  | ATV630C11N4F | 174 | 164 | 173 | 259 | true | C3 | IP21 | 15 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 30
ATV630 | 380-440 V | floor | ND | 132 |  | ATV630C13N4F | 250 | 232 | 250 | 275 | true | C3 | IP21 | 15 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 30
ATV630 | 380-440 V | floor | HD | 110 |  | ATV630C13N4F | 207 | 197 | 211 | 316 | true | C3 | IP21 | 15 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 30
ATV630 | 380-440 V | floor | ND | 160 |  | ATV630C16N4F | 291 | 277 | 302 | 332 | true | C3 | IP21 | 15 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 30
ATV630 | 380-440 V | floor | HD | 132 |  | ATV630C16N4F | 244 | 232 | 250 | 375 | true | C3 | IP21 | 15 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 30
ATV630 | 380-440 V | floor | ND | 200 |  | ATV630C20N4F | 369 | 349 | 370 | 407 | true | C3 | IP21 | 15 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 30
ATV630 | 380-440 V | floor | HD | 160 |  | ATV630C20N4F | 302 | 286 | 302 | 453 | true | C3 | IP21 | 15 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 30
ATV630 | 380-440 V | floor | ND | 250 |  | ATV630C25N4F | 453 | 432 | 477 | 524 | true | C3 | IP21 | 15 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 30
ATV630 | 380-440 V | floor | HD | 200 |  | ATV630C25N4F | 369 | 353 | 370 | 555 | true | C3 | IP21 | 15 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 30
ATV630 | 380-440 V | floor | ND | 315 |  | ATV630C31N4F | 566 | 538 | 590 | 649 | true | C3 | IP21 | 15 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 30
ATV630 | 380-440 V | floor | HD | 250 |  | ATV630C31N4F | 453 | 432 | 477 | 715 | true | C3 | IP21 | 15 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 30
ATV650 | 380-440 V | floor | ND | 110 |  | ATV650C11N4F | 207 | 195 | 211 | 232 | true | C3 | IP54 | 15 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 31
ATV650 | 380-440 V | floor | HD | 90 |  | ATV650C11N4F | 174 | 164 | 173 | 259 | true | C3 | IP54 | 15 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 31
ATV650 | 380-440 V | floor | ND | 132 |  | ATV650C13N4F | 250 | 232 | 250 | 275 | true | C3 | IP54 | 15 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 31
ATV650 | 380-440 V | floor | HD | 110 |  | ATV650C13N4F | 207 | 197 | 211 | 316 | true | C3 | IP54 | 15 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 31
ATV650 | 380-440 V | floor | ND | 160 |  | ATV650C16N4F | 291 | 277 | 302 | 332 | true | C3 | IP54 | 15 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 31
ATV650 | 380-440 V | floor | HD | 132 |  | ATV650C16N4F | 244 | 232 | 250 | 375 | true | C3 | IP54 | 15 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 31
ATV650 | 380-440 V | floor | ND | 200 |  | ATV650C20N4F | 369 | 349 | 370 | 407 | true | C3 | IP54 | 15 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 31
ATV650 | 380-440 V | floor | HD | 160 |  | ATV650C20N4F | 302 | 286 | 302 | 453 | true | C3 | IP54 | 15 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 31
ATV650 | 380-440 V | floor | ND | 250 |  | ATV650C25N4F | 453 | 432 | 477 | 524 | true | C3 | IP54 | 15 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 31
ATV650 | 380-440 V | floor | HD | 200 |  | ATV650C25N4F | 369 | 353 | 370 | 555 | true | C3 | IP54 | 15 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 31
ATV650 | 380-440 V | floor | ND | 315 |  | ATV650C31N4F | 566 | 538 | 590 | 649 | true | C3 | IP54 | 15 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 31
ATV650 | 380-440 V | floor | HD | 250 |  | ATV650C31N4F | 453 | 432 | 477 | 715 | true | C3 | IP54 | 15 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 31
ATV630 | 380-480 V | cabinet_Z | ND | 0.75 | 1 | ATV630U07N4Z | 1.5 | 1.3 | 2.2 | 2.4 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 86
ATV630 | 380-480 V | cabinet_Z | HD | 0.37 | 0.5 | ATV630U07N4Z | 0.9 | 0.8 | 1.5 | 2.3 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 86
ATV630 | 380-480 V | cabinet_Z | ND | 1.5 | 2 | ATV630U15N4Z | 3 | 2.6 | 4 | 4.4 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 86
ATV630 | 380-480 V | cabinet_Z | HD | 0.75 | 1 | ATV630U15N4Z | 1.7 | 1.5 | 2.2 | 3.3 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 86
ATV630 | 380-480 V | cabinet_Z | ND | 2.2 | 3 | ATV630U22N4Z | 4.3 | 3.8 | 5.6 | 6.2 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 86
ATV630 | 380-480 V | cabinet_Z | HD | 1.5 | 2 | ATV630U22N4Z | 3.1 | 2.9 | 4 | 6 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 86
ATV630 | 380-480 V | cabinet_Z | ND | 3 |  | ATV630U30N4Z | 5.8 | 5.1 | 7.2 | 7.9 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 86
ATV630 | 380-480 V | cabinet_Z | HD | 2.2 | 3 | ATV630U30N4Z | 4.5 | 4 | 5.6 | 8.4 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 86
ATV630 | 380-480 V | cabinet_Z | ND | 4 | 5 | ATV630U40N4Z | 7.6 | 6.7 | 9.3 | 10.2 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 86
ATV630 | 380-480 V | cabinet_Z | HD | 3 |  | ATV630U40N4Z | 6 | 5.4 | 7.2 | 10.8 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 86
ATV630 | 380-480 V | cabinet_Z | ND | 5.5 | 7.5 | ATV630U55N4Z | 10.4 | 9.1 | 12.7 | 14 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 86
ATV630 | 380-480 V | cabinet_Z | HD | 4 | 5 | ATV630U55N4Z | 8 | 7.2 | 9.3 | 14 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 86
ATV630 | 380-480 V | cabinet_Z | ND | 7.5 | 10 | ATV630U75N4Z | 13.8 | 11.9 | 16.5 | 18.2 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 86
ATV630 | 380-480 V | cabinet_Z | HD | 5.5 | 7.5 | ATV630U75N4Z | 10.5 | 9.2 | 12.7 | 19.1 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 86
ATV630 | 380-480 V | cabinet_Z | ND | 11 | 15 | ATV630D11N4Z | 19.8 | 17 | 23.5 | 25.9 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 86
ATV630 | 380-480 V | cabinet_Z | HD | 7.5 | 10 | ATV630D11N4Z | 14.1 | 12.5 | 16.5 | 24.8 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 86
ATV630 | 380-480 V | cabinet_Z | ND | 15 | 20 | ATV630D15N4Z | 27 | 23.3 | 31.7 | 34.9 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 86
ATV630 | 380-480 V | cabinet_Z | HD | 11 | 15 | ATV630D15N4Z | 20.6 | 18.1 | 23.5 | 35.3 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 86
ATV630 | 380-480 V | cabinet_Z | ND | 18.5 | 25 | ATV630D18N4Z | 33.4 | 28.9 | 39.2 | 43.1 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 86
ATV630 | 380-480 V | cabinet_Z | HD | 15 | 20 | ATV630D18N4Z | 27.7 | 24.4 | 31.7 | 47.6 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 86
ATV630 | 380-480 V | cabinet_Z | ND | 22 | 30 | ATV630D22N4Z | 39.6 | 34.4 | 46.3 | 50.9 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 86
ATV630 | 380-480 V | cabinet_Z | HD | 18.5 | 25 | ATV630D22N4Z | 34.1 | 29.9 | 39.2 |  | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 86
ATV630 | 380-480 V | cabinet_Z | ND | 30 | 40 | ATV630D30N4Z | 53.3 | 45.9 | 61.5 | 67.7 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 87
ATV630 | 380-480 V | cabinet_Z | HD | 22 | 30 | ATV630D30N4Z | 40.5 | 35.8 | 46.3 | 69.5 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 87
ATV630 | 380-480 V | cabinet_Z | ND | 37 | 50 | ATV630D37N4Z | 66.2 | 57.3 | 74.5 | 82 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 87
ATV630 | 380-480 V | cabinet_Z | HD | 30 | 40 | ATV630D37N4Z | 54.8 | 48.3 | 61.5 | 92.3 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 87
ATV630 | 380-480 V | cabinet_Z | ND | 45 | 60 | ATV630D45N4Z | 79.8 | 69.1 | 88 | 96.8 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 87
ATV630 | 380-480 V | cabinet_Z | HD | 37 | 50 | ATV630D45N4Z | 67.1 | 59 | 74.5 | 111.8 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 87
ATV630 | 380-480 V | cabinet_Z | ND | 55 | 75 | ATV630D55N4Z | 97.2 | 84.2 | 106 | 116.6 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 87
ATV630 | 380-480 V | cabinet_Z | HD | 45 | 60 | ATV630D55N4Z | 81.4 | 71.8 | 88 | 132 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 87
ATV630 | 380-480 V | cabinet_Z | ND | 75 | 100 | ATV630D75N4Z | 131.3 | 112.7 | 145 | 159.5 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 87
ATV630 | 380-480 V | cabinet_Z | HD | 55 | 75 | ATV630D75N4Z | 98.9 | 86.9 | 106 | 159 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 87
ATV630 | 380-480 V | cabinet_Z | ND | 90 | 125 | ATV630D90N4Z | 156.2 | 135.8 | 173 | 190.3 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 87
ATV630 | 380-480 V | cabinet_Z | HD | 75 | 100 | ATV630D90N4Z | 134.3 | 118.1 | 145 | 217.5 | true |  |  | 30 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 87
ATV660 | 380-415 V | system_compact | ND | 110 |  | ATV660C11Q4X1 | 195 |  | 211 | 232 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 113
ATV660 | 380-415 V | system_compact | HD | 90 |  | ATV660C11Q4X1 | 164 |  | 173 | 260 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 113
ATV660 | 380-415 V | system_compact | ND | 132 |  | ATV660C13Q4X1 | 232 |  | 250 | 275 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 113
ATV660 | 380-415 V | system_compact | HD | 110 |  | ATV660C13Q4X1 | 197 |  | 211 | 317 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 113
ATV660 | 380-415 V | system_compact | ND | 160 |  | ATV660C16Q4X1 | 277 |  | 302 | 332 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 113
ATV660 | 380-415 V | system_compact | HD | 132 |  | ATV660C16Q4X1 | 232 |  | 250 | 375 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 113
ATV660 | 380-415 V | system_compact | ND | 200 |  | ATV660C20Q4X1 | 349 |  | 370 | 407 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 113
ATV660 | 380-415 V | system_compact | HD | 160 |  | ATV660C20Q4X1 | 286 |  | 302 | 453 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 113
ATV660 | 380-415 V | system_compact | ND | 250 |  | ATV660C25Q4X1 | 432 |  | 477 | 525 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 113
ATV660 | 380-415 V | system_compact | HD | 200 |  | ATV660C25Q4X1 | 353 |  | 370 | 555 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 113
ATV660 | 380-415 V | system_compact | ND | 315 |  | ATV660C31Q4X1 | 538 |  | 590 | 649 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 113
ATV660 | 380-415 V | system_compact | HD | 250 |  | ATV660C31Q4X1 | 432 |  | 477 | 716 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 113
ATV660 | 380-415 V | system_compact | ND | 355 |  | ATV660C35Q4X1 | 611 |  | 660 | 726 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 113
ATV660 | 380-415 V | system_compact | HD | 280 |  | ATV660C35Q4X1 | 489 |  | 520 | 780 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 113
ATV660 | 380-415 V | system_compact | ND | 400 |  | ATV660C40Q4X1 | 681 |  | 730 | 803 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 113
ATV660 | 380-415 V | system_compact | HD | 315 |  | ATV660C40Q4X1 | 545 |  | 590 | 885 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 113
ATV660 | 380-415 V | system_compact | ND | 450 |  | ATV660C45Q4X1 | 764 |  | 830 | 913 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 113
ATV660 | 380-415 V | system_compact | HD | 355 |  | ATV660C45Q4X1 | 611 |  | 660 | 990 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 113
ATV660 | 380-415 V | system_compact | ND | 500 |  | ATV660C50Q4X1 | 846 |  | 900 | 990 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 113
ATV660 | 380-415 V | system_compact | HD | 400 |  | ATV660C50Q4X1 | 681 |  | 730 | 1095 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 113
ATV660 | 380-415 V | system_compact | ND | 560 |  | ATV660C56Q4X1 | 948 |  | 1020 | 1122 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 113
ATV660 | 380-415 V | system_compact | HD | 450 |  | ATV660C56Q4X1 | 767 |  | 830 | 1245 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 113
ATV660 | 380-415 V | system_compact | ND | 630 |  | ATV660C63Q4X1 | 1058 |  | 1140 | 1254 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 113
ATV660 | 380-415 V | system_compact | HD | 500 |  | ATV660C63Q4X1 | 849 |  | 900 | 1350 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 113
ATV660 | 380-415 V | system_compact | ND | 710 |  | ATV660C71Q4X1 | 1192 |  | 1260 | 1386 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 113
ATV660 | 380-415 V | system_compact | HD | 560 |  | ATV660C71Q4X1 | 951 |  | 1020 | 1530 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 113
ATV660 | 380-415 V | system_compact | ND | 800 |  | ATV660C80Q4X1 | 1335 |  | 1420 | 1562 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 113
ATV660 | 380-415 V | system_compact | HD | 630 |  | ATV660C80Q4X1 | 1061 |  | 1140 | 1710 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 113
ATV660 | 480 V | system_compact | ND | 132 |  | ATV660C11T4X1 | 196 |  | 211 | 232 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 114
ATV660 | 480 V | system_compact | HD | 110 |  | ATV660C11T4X1 | 168 |  | 173 | 260 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 114
ATV660 | 480 V | system_compact | ND | 160 |  | ATV660C13T4X1 | 233 |  | 250 | 275 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 114
ATV660 | 480 V | system_compact | HD | 132 |  | ATV660C13T4X1 | 198 |  | 211 | 317 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 114
ATV660 | 480 V | system_compact | ND | 180 |  | ATV660C16T4X1 | 258 |  | 302 | 332 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 114
ATV660 | 480 V | system_compact | HD | 160 |  | ATV660C16T4X1 | 233 |  | 250 | 375 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 114
ATV660 | 480 V | system_compact | ND | 220 |  | ATV660C20T4X1 | 320 |  | 370 | 407 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 114
ATV660 | 480 V | system_compact | HD | 180 |  | ATV660C20T4X1 | 267 |  | 302 | 453 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 114
ATV660 | 480 V | system_compact | ND | 280 |  | ATV660C25T4X1 | 400 |  | 477 | 525 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 114
ATV660 | 480 V | system_compact | HD | 220 |  | ATV660C25T4X1 | 323 |  | 370 | 555 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 114
ATV660 | 480 V | system_compact | ND | 355 |  | ATV660C31T4X1 | 503 |  | 590 | 649 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 114
ATV660 | 480 V | system_compact | HD | 280 |  | ATV660C31T4X1 | 400 |  | 477 | 716 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 114
ATV660 | 480 V | system_compact | ND | 400 |  | ATV660C35T4X1 | 572 |  | 660 | 726 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 114
ATV660 | 480 V | system_compact | HD | 315 |  | ATV660C35T4X1 | 456 |  | 520 | 780 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 114
ATV660 | 480 V | system_compact | ND | 450 |  | ATV660C40T4X1 | 637 |  | 730 | 803 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 114
ATV660 | 480 V | system_compact | HD | 355 |  | ATV660C40T4X1 | 510 |  | 590 | 885 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 114
ATV660 | 480 V | system_compact | ND | 500 |  | ATV660C45T4X1 | 706 |  | 830 | 913 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 114
ATV660 | 480 V | system_compact | HD | 400 |  | ATV660C45T4X1 | 572 |  | 660 | 990 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 114
ATV660 | 480 V | system_compact | ND | 560 |  | ATV660C50T4X1 | 789 |  | 900 | 990 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 114
ATV660 | 480 V | system_compact | HD | 450 |  | ATV660C50T4X1 | 637 |  | 730 | 1095 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 114
ATV660 | 480 V | system_compact | ND | 630 |  | ATV660C56T4X1 | 888 |  | 1020 | 1122 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 114
ATV660 | 480 V | system_compact | HD | 500 |  | ATV660C56T4X1 | 711 |  | 830 | 1245 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 114
ATV660 | 480 V | system_compact | ND | 710 |  | ATV660C63T4X1 | 993 |  | 1140 | 1254 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 114
ATV660 | 480 V | system_compact | HD | 560 |  | ATV660C63T4X1 | 794 |  | 900 | 1350 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 114
ATV660 | 480 V | system_compact | ND | 800 |  | ATV660C71T4X1 | 1119 |  | 1260 | 1386 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 114
ATV660 | 480 V | system_compact | HD | 630 |  | ATV660C71T4X1 | 893 |  | 1020 | 1530 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 114
ATV660 | 480 V | system_compact | ND | 900 |  | ATV660C80T4X1 | 1257 |  | 1420 | 1562 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 114
ATV660 | 480 V | system_compact | HD | 710 |  | ATV660C80T4X1 | 997 |  | 1140 | 1710 | false |  | IP23 | 0 | true | Catalog Altivar Process ATV600 variable speed drives.pdf | 114
ATV680 | 380-415 V | system_LH | ND | 110 |  | ATV680C11Q4X1 | 175 |  | 211 | 232 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 119
ATV680 | 380-415 V | system_LH | HD | 90 |  | ATV680C11Q4X1 | 144 |  | 173 | 260 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 119
ATV680 | 380-415 V | system_LH | ND | 132 |  | ATV680C13Q4X1 | 208 |  | 250 | 275 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 119
ATV680 | 380-415 V | system_LH | HD | 110 |  | ATV680C13Q4X1 | 174 |  | 211 | 317 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 119
ATV680 | 380-415 V | system_LH | ND | 160 |  | ATV680C16Q4X1 | 252 |  | 302 | 332 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 119
ATV680 | 380-415 V | system_LH | HD | 132 |  | ATV680C16Q4X1 | 208 |  | 250 | 375 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 119
ATV680 | 380-415 V | system_LH | ND | 200 |  | ATV680C20Q4X1 | 313 |  | 370 | 407 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 119
ATV680 | 380-415 V | system_LH | HD | 160 |  | ATV680C20Q4X1 | 252 |  | 302 | 453 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 119
ATV680 | 380-415 V | system_LH | ND | 250 |  | ATV680C25Q4X1 | 389 |  | 477 | 525 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 119
ATV680 | 380-415 V | system_LH | HD | 200 |  | ATV680C25Q4X1 | 313 |  | 370 | 555 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 119
ATV680 | 380-415 V | system_LH | ND | 315 |  | ATV680C31Q4X1 | 491 |  | 590 | 649 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 119
ATV680 | 380-415 V | system_LH | HD | 250 |  | ATV680C31Q4X1 | 389 |  | 477 | 716 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 119
ATV680 | 380-415 V | system_LH | ND | 355 |  | ATV680C35Q4X1 | 553 |  | 660 | 726 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 119
ATV680 | 380-415 V | system_LH | HD | 280 |  | ATV680C35Q4X1 | 436 |  | 520 | 780 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 119
ATV680 | 380-415 V | system_LH | ND | 400 |  | ATV680C40Q4X1 | 620 |  | 730 | 803 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 119
ATV680 | 380-415 V | system_LH | HD | 315 |  | ATV680C40Q4X1 | 491 |  | 590 | 885 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 119
ATV680 | 380-415 V | system_LH | ND | 450 |  | ATV680C45Q4X1 | 697 |  | 830 | 913 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 119
ATV680 | 380-415 V | system_LH | HD | 355 |  | ATV680C45Q4X1 | 553 |  | 660 | 990 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 119
ATV680 | 380-415 V | system_LH | ND | 500 |  | ATV680C50Q4X1 | 775 |  | 900 | 990 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 119
ATV680 | 380-415 V | system_LH | HD | 400 |  | ATV680C50Q4X1 | 620 |  | 730 | 1095 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 119
ATV680 | 380-415 V | system_LH | ND | 560 |  | ATV680C56Q4X1 | 868 |  | 1020 | 1122 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 119
ATV680 | 380-415 V | system_LH | HD | 450 |  | ATV680C56Q4X1 | 697 |  | 830 | 1245 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 119
ATV680 | 380-415 V | system_LH | ND | 630 |  | ATV680C63Q4X1 | 971 |  | 1140 | 1254 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 119
ATV680 | 380-415 V | system_LH | HD | 500 |  | ATV680C63Q4X1 | 775 |  | 900 | 1350 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 119
ATV680 | 380-415 V | system_LH | ND | 710 |  | ATV680C71Q4X1 | 1094 |  | 1260 | 1386 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 119
ATV680 | 380-415 V | system_LH | HD | 560 |  | ATV680C71Q4X1 | 868 |  | 1020 | 1530 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 119
ATV680 | 380-415 V | system_LH | ND | 800 |  | ATV680C80Q4X1 | 1227 |  | 1420 | 1562 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 119
ATV680 | 380-415 V | system_LH | HD | 630 |  | ATV680C80Q4X1 | 971 |  | 1140 | 1710 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 119
ATV680 | 480 V | system_LH | ND | 132 |  | ATV680C11T4X1 | 175 |  | 211 | 232 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 120
ATV680 | 480 V | system_LH | HD | 110 |  | ATV680C11T4X1 | 147 |  | 173 | 260 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 120
ATV680 | 480 V | system_LH | ND | 160 |  | ATV680C13T4X1 | 211 |  | 250 | 275 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 120
ATV680 | 480 V | system_LH | HD | 132 |  | ATV680C13T4X1 | 175 |  | 211 | 317 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 120
ATV680 | 480 V | system_LH | ND | 180 |  | ATV680C16T4X1 | 236 |  | 302 | 332 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 120
ATV680 | 480 V | system_LH | HD | 160 |  | ATV680C16T4X1 | 211 |  | 250 | 375 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 120
ATV680 | 480 V | system_LH | ND | 220 |  | ATV680C20T4X1 | 287 |  | 370 | 407 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 120
ATV680 | 480 V | system_LH | HD | 180 |  | ATV680C20T4X1 | 236 |  | 302 | 453 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 120
ATV680 | 480 V | system_LH | ND | 280 |  | ATV680C25T4X1 | 363 |  | 477 | 525 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 120
ATV680 | 480 V | system_LH | HD | 220 |  | ATV680C25T4X1 | 287 |  | 370 | 555 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 120
ATV680 | 480 V | system_LH | ND | 355 |  | ATV680C31T4X1 | 461 |  | 590 | 649 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 120
ATV680 | 480 V | system_LH | HD | 280 |  | ATV680C31T4X1 | 363 |  | 477 | 716 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 120
ATV680 | 480 V | system_LH | ND | 400 |  | ATV680C35T4X1 | 519 |  | 660 | 726 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 120
ATV680 | 480 V | system_LH | HD | 315 |  | ATV680C35T4X1 | 409 |  | 520 | 780 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 120
ATV680 | 480 V | system_LH | ND | 450 |  | ATV680C40T4X1 | 581 |  | 730 | 803 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 120
ATV680 | 480 V | system_LH | HD | 355 |  | ATV680C40T4X1 | 461 |  | 590 | 885 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 120
ATV680 | 480 V | system_LH | ND | 500 |  | ATV680C45T4X1 | 646 |  | 830 | 913 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 120
ATV680 | 480 V | system_LH | HD | 400 |  | ATV680C45T4X1 | 519 |  | 660 | 990 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 120
ATV680 | 480 V | system_LH | ND | 560 |  | ATV680C50T4X1 | 723 |  | 900 | 990 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 120
ATV680 | 480 V | system_LH | HD | 450 |  | ATV680C50T4X1 | 581 |  | 730 | 1095 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 120
ATV680 | 480 V | system_LH | ND | 630 |  | ATV680C56T4X1 | 813 |  | 1020 | 1122 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 120
ATV680 | 480 V | system_LH | HD | 500 |  | ATV680C56T4X1 | 646 |  | 830 | 1245 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 120
ATV680 | 480 V | system_LH | ND | 710 |  | ATV680C63T4X1 | 912 |  | 1140 | 1254 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 120
ATV680 | 480 V | system_LH | HD | 560 |  | ATV680C63T4X1 | 723 |  | 900 | 1350 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 120
ATV680 | 480 V | system_LH | ND | 800 |  | ATV680C71T4X1 | 1028 |  | 1260 | 1386 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 120
ATV680 | 480 V | system_LH | HD | 630 |  | ATV680C71T4X1 | 813 |  | 1020 | 1530 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 120
ATV680 | 480 V | system_LH | ND | 900 |  | ATV680C80T4X1 | 1150 |  | 1420 | 1562 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 120
ATV680 | 480 V | system_LH | HD | 710 |  | ATV680C80T4X1 | 912 |  | 1140 | 1710 | false |  | IP23 | 5 | false | Catalog Altivar Process ATV600 variable speed drives.pdf | 120

## passive_filters
motor_kw | motor_hp | for_drive_refs | filter_current_in_a | filter_current_out_a | quantity_per_drive | filter_reference | supply | thdi_note | source_pdf | source_page
0.75 | 1 | ATV630U07N4¦ATV650U07N4¦ATV650U07N4E | 6 | 6.2 | 1 | VW3A46101 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 52
1.5 | 2 | ATV630U15N4¦ATV650U15N4¦ATV650U15N4E | 10 | 10.4 | 1 | VW3A46102 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 52
2.2 | 3 | ATV630U22N4¦ATV650U22N4¦ATV650U22N4E | 10 | 10.4 | 1 | VW3A46102 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 52
3 |  | ATV630U30N4¦ATV650U30N4¦ATV650U30N4E | 10 | 10.4 | 1 | VW3A46102 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 52
4 | 5 | ATV630U40N4¦ATV650U40N4¦ATV650U40N4E | 10 | 10.4 | 1 | VW3A46102 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 52
5.5 | 7.5 | ATV630U55N4¦ATV650U55N4¦ATV650U55N4E | 14 | 14.5 | 1 | VW3A46103 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 52
7.5 | 10 | ATV630U75N4¦ATV650U75N4¦ATV650U75N4E | 14 | 14.5 | 1 | VW3A46103 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 52
11 | 15 | ATV630D11N4¦ATV650D11N4¦ATV650D11N4E | 22 | 23 | 1 | VW3A46104 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 52
15 | 20 | ATV630D15N4¦ATV650D15N4¦ATV650D15N4E | 29 | 30 | 1 | VW3A46105 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 52
18.5 | 25 | ATV630D18N4¦ATV650D18N4¦ATV650D18N4E | 35 | 37 | 1 | VW3A46106 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 52
22 | 30 | ATV630D22N4¦ATV650D22N4¦ATV650D22N4E | 43 | 45 | 1 | VW3A46107 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 52
30 | 40 | ATV630D30N4¦ATV650D30N4¦ATV650D30N4E | 58 | 60 | 1 | VW3A46108 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 52
37 | 50 | ATV630D37N4¦ATV650D37N4¦ATV650D37N4E | 72 | 75 | 1 | VW3A46109 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 52
45 | 60 | ATV630D45N4¦ATV650D45N4¦ATV650D45N4E | 86 | 90 | 1 | VW3A46110 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 52
55 | 75 | ATV630D55N4¦ATV650D55N4¦ATV650D55N4E | 101 | 105 | 1 | VW3A46111 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 52
75 | 100 | ATV630D75N4¦ATV650D75N4¦ATV650D75N4E | 144 | 150 | 1 | VW3A46112 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 52
90 | 125 | ATV630D90N4¦ATV650D90N4¦ATV650D90N4E | 180 | 187 | 1 | VW3A46113 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 52
110 | 150 | ATV630C11N4 | 217 | 225 | 1 | VW3A46114 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 52
132 | 200 | ATV630C13N4 | 252 | 262 | 1 | VW3A46115 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 52
160 | 250 | ATV630C16N4 | 304 | 316 | 1 | VW3A46116 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 52
220 | 350 | ATV630C22N4 | 380 | 395 | 1 | VW3A46118 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 52
250 | 400 | ATV630C25N4 | 433 | 450 | 1 | VW3A46119 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 52
315 | 500 | ATV630C31N4 | 304 | 316 | 2 | VW3A46116 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 52
[5 empty] | 1 | VW3A46106 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 52
0.75 | 1 | ATV630U07N4¦ATV650U07N4¦ATV650U07N4E | 6 | 6.2 | 1 | VW3A46120 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 53
1.5 | 2 | ATV630U15N4¦ATV650U15N4¦ATV650U15N4E | 10 | 10.4 | 1 | VW3A46121 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 53
2.2 | 3 | ATV630U22N4¦ATV650U22N4¦ATV650U22N4E | 10 | 10.4 | 1 | VW3A46121 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 53
3 |  | ATV630U30N4¦ATV650U30N4¦ATV650U30N4E | 10 | 10.4 | 1 | VW3A46121 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 53
4 | 5 | ATV630U40N4¦ATV650U40N4¦ATV650U40N4E | 10 | 10.4 | 1 | VW3A46121 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 53
5.5 | 7.5 | ATV630U55N4¦ATV650U55N4¦ATV650U55N4E | 14 | 14.5 | 1 | VW3A46122 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 53
7.5 | 10 | ATV630U75N4¦ATV650U75N4¦ATV650U75N4E | 14 | 14.5 | 1 | VW3A46122 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 53
11 | 15 | ATV630D11N4¦ATV650D11N4¦ATV650D11N4E | 22 | 23 | 1 | VW3A46123 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 53
15 | 20 | ATV630D15N4¦ATV650D15N4¦ATV650D15N4E | 29 | 30 | 1 | VW3A46124 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 53
18.5 | 25 | ATV630D18N4¦ATV650D18N4¦ATV650D18N4E | 35 | 37 | 1 | VW3A46125 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 53
22 | 30 | ATV630D22N4¦ATV650D22N4¦ATV650D22N4E | 43 | 45 | 1 | VW3A46126 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 53
30 | 40 | ATV630D30N4¦ATV650D30N4¦ATV650D30N4E | 58 | 60 | 1 | VW3A46127 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 53
37 | 50 | ATV630D37N4¦ATV650D37N4¦ATV650D37N4E | 72 | 75 | 1 | VW3A46128 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 53
45 | 60 | ATV630D45N4¦ATV650D45N4¦ATV650D45N4E | 86 | 90 | 1 | VW3A46129 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 53
55 | 75 | ATV630D55N4¦ATV650D55N4¦ATV650D55N4E | 101 | 105 | 1 | VW3A46130 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 53
75 | 100 | ATV630D75N4¦ATV650D75N4¦ATV650D75N4E | 144 | 150 | 1 | VW3A46131 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 53
90 | 125 | ATV630D90N4¦ATV650D90N4¦ATV650D90N4E | 180 | 187 | 1 | VW3A46132 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 53
110 | 150 | ATV630C11N4 | 217 | 225 | 1 | VW3A46133 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 53
132 | 200 | ATV630C13N4 | 252 | 262 | 1 | VW3A46134 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 53
160 | 250 | ATV630C16N4 | 304 | 316 | 1 | VW3A46135 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 53
220 | 350 | ATV630C22N4 | 380 | 395 | 1 | VW3A46137 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 53
250 | 400 | ATV630C25N4 | 433 | 450 | 1 | VW3A46138 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 53
315 | 500 | ATV630C31N4 | 304 | 316 | 2 | VW3A46135 | 400 V 50 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 53
0.75 | 1 | ATV630U07N4¦ATV650U07N4¦ATV650U07N4E | 6 | 6.2 | 1 | VW3A46139 | 460 V 60 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 54
1.5 | 2 | ATV630U15N4¦ATV650U15N4¦ATV650U15N4E | 10 | 10.4 | 1 | VW3A46140 | 460 V 60 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 54
2.2 | 3 | ATV630U22N4¦ATV650U22N4¦ATV650U22N4E | 10 | 10.4 | 1 | VW3A46140 | 460 V 60 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 54
3 |  | ATV630U30N4¦ATV650U30N4¦ATV650U30N4E | 10 | 10.4 | 1 | VW3A46140 | 460 V 60 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 54
4 | 5 | ATV630U40N4¦ATV650U40N4¦ATV650U40N4E | 10 | 10.4 | 1 | VW3A46140 | 460 V 60 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 54
5.5 | 7.5 | ATV630U55N4¦ATV650U55N4¦ATV650U55N4E | 14 | 14.5 | 1 | VW3A46141 | 460 V 60 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 54
7.5 | 10 | ATV630U75N4¦ATV650U75N4¦ATV650U75N4E | 14 | 14.5 | 1 | VW3A46141 | 460 V 60 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 54
11 | 15 | ATV630D11N4¦ATV650D11N4¦ATV650D11N4E | 19 | 19.5 | 1 | VW3A46142 | 460 V 60 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 54
15 | 20 | ATV630D15N4¦ATV650D15N4¦ATV650D15N4E | 25 | 26 | 1 | VW3A46143 | 460 V 60 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 54
18.5 | 25 | ATV630D18N4¦ATV650D18N4¦ATV650D18N4E | 31 | 32 | 1 | VW3A46144 | 460 V 60 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 54
22 | 30 | ATV630D22N4¦ATV650D22N4¦ATV650D22N4E | 36 | 37 | 1 | VW3A46145 | 460 V 60 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 54
30 | 40 | ATV630D30N4¦ATV650D30N4¦ATV650D30N4E | 48 | 50 | 1 | VW3A46146 | 460 V 60 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 54
37 | 50 | ATV630D37N4¦ATV650D37N4¦ATV650D37N4E | 60 | 62 | 1 | VW3A46147 | 460 V 60 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 54
45 | 60 | ATV630D45N4¦ATV650D45N4¦ATV650D45N4E | 73 | 76 | 1 | VW3A46148 | 460 V 60 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 54
55 | 75 | ATV630D55N4¦ATV650D55N4¦ATV650D55N4E | 95 | 99 | 1 | VW3A46149 | 460 V 60 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 54
75 | 100 | ATV630D75N4¦ATV650D75N4¦ATV650D75N4E | 118 | 122 | 1 | VW3A46150 | 460 V 60 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 54
90 | 125 | ATV630D90N4¦ATV650D90N4¦ATV650D90N4E | 154 | 160 | 1 | VW3A46151 | 460 V 60 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 54
110 | 150 | ATV630C11N4 | 183 | 190 | 1 | VW3A46152 | 460 V 60 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 54
132 | 200 | ATV630C13N4 | 231 | 240 | 1 | VW3A46153 | 460 V 60 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 54
160 | 250 | ATV630C16N4 | 291 | 302.5 | 1 | VW3A46154 | 460 V 60 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 54
220 | 350 | ATV630C22N4 | 355 | 369 | 1 | VW3A46155 | 460 V 60 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 54
250 | 400 | ATV630C25N4 | 436 | 450 | 1 | VW3A46157 | 460 V 60 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 54
315 | 500 | ATV630C31N4 | 231 | 240 | 2 | VW3A46153 | 460 V 60 Hz |  | Catalog Altivar Process ATV600 variable speed drives.pdf | 54
0.75 | 1 | ATV630U07N4¦ATV650U07N4¦ATV650U07N4E | 6 | 6.2 | 1 | VW3A46158 | 460 V 60 Hz | <5% | Catalog Altivar Process ATV600 variable speed drives.pdf | 55
1.5 | 2 | ATV630U15N4¦ATV650U15N4¦ATV650U15N4E | 10 | 10.4 | 1 | VW3A46159 | 460 V 60 Hz | <5% | Catalog Altivar Process ATV600 variable speed drives.pdf | 55
2.2 | 3 | ATV630U22N4¦ATV650U22N4¦ATV650U22N4E | 10 | 10.4 | 1 | VW3A46159 | 460 V 60 Hz | <5% | Catalog Altivar Process ATV600 variable speed drives.pdf | 55
3 |  | ATV630U30N4¦ATV650U30N4¦ATV650U30N4E | 10 | 10.4 | 1 | VW3A46159 | 460 V 60 Hz | <5% | Catalog Altivar Process ATV600 variable speed drives.pdf | 55
4 | 5 | ATV630U40N4¦ATV650U40N4¦ATV650U40N4E | 10 | 10.4 | 1 | VW3A46159 | 460 V 60 Hz | <5% | Catalog Altivar Process ATV600 variable speed drives.pdf | 55
5.5 | 7.5 | ATV630U55N4¦ATV650U55N4¦ATV650U55N4E | 14 | 14.5 | 1 | VW3A46160 | 460 V 60 Hz | <5% | Catalog Altivar Process ATV600 variable speed drives.pdf | 55
7.5 | 10 | ATV630U75N4¦ATV650U75N4¦ATV650U75N4E | 14 | 14.5 | 1 | VW3A46160 | 460 V 60 Hz | <5% | Catalog Altivar Process ATV600 variable speed drives.pdf | 55
11 | 15 | ATV630D11N4¦ATV650D11N4¦ATV650D11N4E | 19 | 19.5 | 1 | VW3A46161 | 460 V 60 Hz | <5% | Catalog Altivar Process ATV600 variable speed drives.pdf | 55
15 | 20 | ATV630D15N4¦ATV650D15N4¦ATV650D15N4E | 25 | 26 | 1 | VW3A46162 | 460 V 60 Hz | <5% | Catalog Altivar Process ATV600 variable speed drives.pdf | 55
18.5 | 25 | ATV630D18N4¦ATV650D18N4¦ATV650D18N4E | 31 | 32 | 1 | VW3A46163 | 460 V 60 Hz | <5% | Catalog Altivar Process ATV600 variable speed drives.pdf | 55
22 | 30 | ATV630D22N4¦ATV650D22N4¦ATV650D22N4E | 36 | 37 | 1 | VW3A46164 | 460 V 60 Hz | <5% | Catalog Altivar Process ATV600 variable speed drives.pdf | 55
30 | 40 | ATV630D30N4¦ATV650D30N4¦ATV650D30N4E | 48 | 50 | 1 | VW3A46165 | 460 V 60 Hz | <5% | Catalog Altivar Process ATV600 variable speed drives.pdf | 55
37 | 50 | ATV630D37N4¦ATV650D37N4¦ATV650D37N4E | 60 | 62 | 1 | VW3A46166 | 460 V 60 Hz | <5% | Catalog Altivar Process ATV600 variable speed drives.pdf | 55
45 | 60 | ATV630D45N4¦ATV650D45N4¦ATV650D45N4E | 73 | 76 | 1 | VW3A46167 | 460 V 60 Hz | <5% | Catalog Altivar Process ATV600 variable speed drives.pdf | 55
55 | 75 | ATV630D55N4¦ATV650D55N4¦ATV650D55N4E | 95 | 99 | 1 | VW3A46168 | 460 V 60 Hz | <5% | Catalog Altivar Process ATV600 variable speed drives.pdf | 55
75 | 100 | ATV630D75N4¦ATV650D75N4¦ATV650D75N4E | 118 | 122 | 1 | VW3A46169 | 460 V 60 Hz | <5% | Catalog Altivar Process ATV600 variable speed drives.pdf | 55
90 | 125 | ATV630D90N4¦ATV650D90N4¦ATV650D90N4E | 154 | 160 | 1 | VW3A46170 | 460 V 60 Hz | <5% | Catalog Altivar Process ATV600 variable speed drives.pdf | 55
110 | 150 | ATV630C11N4 | 183 | 190 | 1 | VW3A46171 | 460 V 60 Hz | <5% | Catalog Altivar Process ATV600 variable speed drives.pdf | 55
132 | 200 | ATV630C13N4 | 231 | 240 | 1 | VW3A46172 | 460 V 60 Hz | <5% | Catalog Altivar Process ATV600 variable speed drives.pdf | 55
160 | 250 | ATV630C16N4 | 291 | 316 | 1 | VW3A46173 | 460 V 60 Hz | <5% | Catalog Altivar Process ATV600 variable speed drives.pdf | 55
220 | 350 | ATV630C22N4 | 355 | 369 | 1 | VW3A46174 | 460 V 60 Hz | <5% | Catalog Altivar Process ATV600 variable speed drives.pdf | 55
250 | 400 | ATV630C25N4 | 436 | 450 | 1 | VW3A46176 | 460 V 60 Hz | <5% | Catalog Altivar Process ATV600 variable speed drives.pdf | 55
315 | 500 | ATV630C31N4 | 231 | 240 | 2 | VW3A46172 | 460 V 60 Hz | <5% | Catalog Altivar Process ATV600 variable speed drives.pdf | 55

## NOTES
Part 1 catalog extract notes
Primary KPI = drive commercial Reference.
Variant default: is_default_variant=true prefers normal Process (not …Z cabinet) for same kW/duty/supply.
DC choke: has_dc_choke is a FEATURE FLAG only. Client PDFs have no DC-choke accessory SKU table.
Catalog p.17: embedded DC choke on 380…480 V Process offer; ATV680/ATV660 marked false.
Passive filters: secondary accessory KPI (VW3A461…).
Getting Started PDF: not used (no rating tables).
Installation manual: reserved for Part 2 gold validation cross-check.
Source: Catalog Altivar Process ATV600 variable speed drives.pdf
Drive pages extracted: 24-31, 86-87, 113-114, 119-120
Filter pages extracted: 52-55