Project : Export Bank VSD

Date :

Compliance sheet

| Item | Specs | Electra Control Reply |
| --- | --- | --- |
| 2.1 | VARIABLE SPEED (FREQUENCY) DRIVES (VSDs) |  |
| 2.10.1 | GENERAL: |  |
| A | The frequency drive shall employ Pulse Width Modulation (PWM), or Pulse Vector Modulation (PVM) using thyristor or transistor switches. | Comply |
| B | The rating of the frequency drive shall be sufficient for the continuous maximum rating of the motor and not it's running load. | Comply as we select the VSD higher than the Motor rating due to the derating of the ambient temp |
| C | The frequency drive unit shall have efficiency in excess of 90 %. | Comply with higher than 96 % look at annex No 1 (All the ATV630 efficiency ratings) |
| D | The frequency drive shall be capable of switching on to a motor already rotating. in either direction. | Comply |
| E | The contractor shall calculate the maximum heat dissipation from all VSDs and incorporate adequate ventilation (or cooling if needed) methods to ensure that the internal temperature within the drive does not exceed 35°C. The calculations shall be submitted for consultant approval. | Please check heat dissipation section also look at the Annex no 2 for all selected VSD heat dissipation & Air flow |
| 2.10.2 | TECHNICAL FEATURES |  |
| A | The input to the frequency drive shall be of an uncontrolled bridge rectifier. type, to limit harmonic distortion. | Comply also we have a built in DC choke to comply with IEC 61000-3-12 |
| B | The speed shall be smoothly adjustable, and controlled by one of the following: |  |
|  | 1. Potentiometer (Manual/hand operation) | Comply via VFD keypad |
|  | 2. 0-10V dc signal (Auto operation) | Comply using the Analogue inputs on control card |
|  | 3. 4-20 m A signal (Auto operation) | Comply using the Analogue inputs on control card |

| C | Overcurrent, short-circuit and earth fault protection of the output shall be provided within the control system. Reset of any fault condition shall be manual. | Comply, look at annex No 3 for all the warning & error codes that VSD protect against |
| --- | --- | --- |
| D | The system shall provide protection against phase loss. If not included within the frequency drive, then an external phase loss detection device shall be fitted. | Comply, protection functions are listed on each VSD data sheet |
| E | Full rated output shall be provided continuously with an ambient temperature of 50 oC and 90% relative humidity the control panel manufacturer shall ensure that sections of the panels housing frequency drives shall be suitably ventilated and/or cooling to ensure that this temperature is not exceeded. | E. Comply. The VFD proposed to give its continuous rated current at room ambient of 50C and derating is applied look at the derating part |
| F | The starting arrangement shall include a ramp speed control, to achieve starting currents not exceeding normal full load current wherever possible. | Comply |
| G | The output frequency range shall nominally be 0.5 to 120 Hz. | Comply, look at each VSD data sheet to find Speed drive output frequency 0.1…500 Hz |
| H | The variable speed drive digital display screen shall provide the following visual. information: |  |
|  | Motor Speed, Motor Power (kW), Motor full load frequency loading percentage, and actual drawn current. | Comply using different types of display: digital, bar, list |
| I | The VSD shall be capable of providing the following points to the BMS: | Comply look at annex No 4 for all the display parameters |
|  | a. Motor fault (short circuit, overload, phase failure, and overheat). | Comply |
|  | b. Motor status (Running). | Comply |
|  | c. Motor reference analogue pints (speed, power, current, and loading percentage). | Comply |
| J | The VSD shall be equipped with standard communication protocol for full. interface with BMS (Bacnet, LON, or ModBus). | Comply with Modbus/TCP, Modbus serial link with two different ports , look at Annex No 5 |
| K | The control circuits shall be immune to interference caused by operating on normal raw mains supply in an industrial environment. | ATV6 0 have built-in Category C2 and C3 EMC filter. All VFDs comply with EN/IEC 61800-3 |

| L | Where variable speed drives systems might be a source of Radio Frequency Interference (RFI) sufficient to interfere with the proposed functioning of adjacent computer-based equipment, RFI suppression at source shall be applied. | ATV6 0 have built-in Category C2 and C3 EMC filter. All VFDs comply with EN/IEC 61800-3 |
| --- | --- | --- |
| M | VSDs shall be equipped with harmonics filters to ensure a maximum of 5% deviation in current. | Comply with IEEE519 using the selected passive filters with THDi > 5 % |
| N | The manufacturer shall provide details regarding the production of mains-borne interference and harmonic. Written guarantees shall be given by the manufacturer that these levels of interference and harmonics shall not be exceeded over the full operating speed of the drive. | Altivar Process drives have an integrated radio interference input filters in accordance with the EMC standard for variable speed electrical power drive in environment 1 or 2, and to comply with the European EMC (electromagnetic compatibility) directive. ATV6 0 have also embedded low harmonic DC choke technology complying with standard IEC 61000-3-12 |
| O | Where screening of cables between the frequency drive and motor to the MCC is required, the type of cable recommended must be indicated at the tender stage. The recommended shielded type cable must ensure that the level of any radio interference is limited to comply with BS EN 55015. | Cables are out of VFD scope of supply |
| P | The harmonic current spectrum of each frequency drive shall be provided by the manufacturer for the calculation and provision of suitable filtration at the electrical switchboard. | We already used a Low Harmonics drives using the ATV630 + passive filters with THDi > 5 % |
| Q | All drives shall be IP-54, unless otherwise mentioned. | Comply using the ATV630 inside a IP55 panels |