| Low Voltage Variable Speed Drive |  |
| --- | --- |
| 1- General |  |
| Specs Points | Schneider Electric Comment |
| Furnish complete variable frequency drives as specified herein for the pumps designated to be variable speed. All standards and optional features shall be included within the VFD enclosure. The drive panel shall be free-stand with IP 54. | The ATV680 Low Harmonic Drive Systems are used when drives should contain mains harmonics particularly low. In comparison with the classic circuit structure of active mains rectifiers, the 3- level technology allows an increase of the switching frequency and the current load is reduced at the same time. This new technology reaches a total distortion factor THD(i) of around 2 % and thus fulfills the requirements according to IEEE 519 of THD(i) < 5 % also in case of distorted mains. Additionally, the cos Phi ≈ 1 in each load situation helps to reduce the load of the mains. IP54 drives is used as per the technical offer |
| VFD is to be provided for motor starting and speed control where shown on electrical or mechanical drawings. Necessary interfaces and accessories to be provided for communication with the SCADA system. | Comply , with built in Ethernet IP & Modbus TCP ports |
| VFD shall convert three-phase, 50 hertz utility power to adjustable voltage and frequency, three phase power for stepless motor speed control from 10% to 100% of the motor's 50 hertz speed. Input voltage shall be as specified on the drawing schedules. | Comply as per below : Voltage ranges l 3 AC 380 V -10 % ... 415 V +6 % l 3 AC 400 V -10 % ... 415 V +10 % l 3 AC 440 V ±10 % l 3 AC 480 V ±10 % Mains frequency 50/60 Hz +/- 5 % Output frequency 0.1…500 Hz |
| The VFD shall be with built-in active harmonics filter at the rectifier & inverter units (Low Harmonic Type). The harmonic filter configuration shall result in a current waveform that approximates near sinusoidal input current waveform and compliant with requirements of IEEE 519. The power section shall be insensitive to phase rotation of the AC line. Total harmonic voltage distortion less than 3%. | Comply using ATV680 our LH drive system that comply with IEEE519 specs The ATV680 includes an active input bridge and leads a sinusoidal mains current. So it is an alternative to active and passive filters. State-of-the-art components, a new control concept as well as a top-quality filter module reduce the total harmonic distortion THD(i) of the frequency inverter to a value less than 2...5 % and by this way it fulfills the requirements according to the recommendations in IEEE 519 to reduce the current harmonics in the mains. Also in case of operation with partial load (from 30 % Pn) the ATV680 leads a sinusoidal mains current with a power factor cos Phi ≈ 1. |
| VFD shall be type tested, certification should be submitted | Comply , Certificate is attached on the technical offer |
| Enclosure should be fully closed metal casing shall be made of four pre-lacquered, hot- galvanized steel plate sections 2 mm thick to optimize heat exchange | Comply using our SFN Spacial panel with IP54 ,RAL 7035 , IK10 for plain door and IK08 for transparent door according to IEC 62262 |
| The output power section shall change fixed DC voltage to adjustable frequency AC voltage. This section shall use insulated gate bipolar transistors (IGBT) or intelligent power modules (IPM) as required by the current rating of the motor | Comply , Attached the Structure of the ATV680 with the AFE & DC and the output IGBT |
| VFD shall include a converter and an inverter section. The converter section shall convert fixed frequency and voltage AC utility power to DC voltage. All VFDs shall include input line reactors or an isolation transformer as required. The inverter section of the VFD shall invert the DC voltage into a quality output waveform, with adjustable voltage and frequency for stepless motor speed control. The VFD shall maintain a constant V/Hz ratio. The VFD and options shall be tested to ANSI/UL.508. The complete drive, including all specified options, shall be listed by a nationally recognized testing agency such as UL or ETL | Comply , EU Certification , UL Certification for ATV680 are attached on the technical offer . The 3-level technology of the active mains rectifier reduces the voltage load at the motor significantly compared to other Low Harmonic frequency inverters. The gliding adaptation of the DC link voltage makes a major contribution to extend the motor lifetime |
| Power line noise shall be limited to a voltage distortion factor and line notch as defined in IEEE 519, "Recommended Practices and requirements for harmonic control in electrical power systems". The total voltage distortion shall not exceed 3 percent. The total feedback harmonics not to exceed 10%. | The ATV680 Low Harmonic Drive Systems are used when drives should contain mains harmonics particularly low. In comparison with the classic circuit structure of active mains rectifiers, the 3- level technology allows an increase of the switching frequency and the current load is reduced at the same time. This new technology reaches a total distortion factor THD(i) of around 2 % and thus fulfills the requirements according to IEEE 519 of THD(i) < 5 % also in case of distorted mains. Additionally, the cos Phi ≈ 1 in each load situation helps to reduce the load of the mains. |
| The VFD shall not emit radiated RFI in excess of the limitations set forth in the FCC Rules and Regulations, FCC Part 15 for Class A computing devices. The VFD shall carry a FCC compliance label. PWM type drives shall include RFI filters. | Built in EMC filter to comply with EMC immunity According to EN 61800-3, second environment (EN 61000-4-2; EN 61000-4-3; EN 61000-4-4; EN 61000-4-5; EN 61000-4-6) EMC emission In accordance with product standard EN 61800-3, second environment, category C3 |
| Motor noise as a result of the VFD shall be limited to 3 dB over across the line operation measured at 1 meter from the motor's centerline | Comply using motor noise reduction function [Noise Reduction] NRD Random frequency modulation helps to prevent any resonance, which may occur at a fixed frequency. |
| VFD's full load amp rating shall meet or exceed NFPA 70, NEC Table 430-150. | Noted as per the selection of the VSD according to the Project BOQ |
| Protective Features shall include: a) Individual motor overload protection for each motor controlled. b) Protection against input power under-voltage, over-voltage, and phase loss. c) Protection against output current overload and instantaneous over-current. d) Protection against over-temperature within the VFD enclosure. e) Protection against over-voltage on the DC bus. f) Thermistor motor protection relay interface. g) Protect VFD from sustained power of phase loss. Under-voltage trip activates automatically when line voltage drops more than 10 percent below rated input voltage. h) Automatically reset faults due to under-voltage, over-voltage, phase loss, or over temperature. i) 9. Protection against output short circuit and motor winding shorting to case faults, as defined by UL 508. j) Status lights or digital display for indication of individual fault conditions. k) Controller capable of operating without a motor or any other equipment connected to the drive output to facilitate start-up and troubleshooting. l) Input line reactors shall be provided to minimize harmonics introduced to the AC line and to provide additional protection to AC line transients. | Comply for all points a,b,c,d,e,f,g,h,i,j,k,l Attached also all the warnings & Fault functions of ATV680 |
| Interface Features for the VFD will include: a) Door mounted Hand/Off/Auto selector switch to start and stop the VFD. In the Auto position, the VFD will start/stop from the controller. In the Hand position, the VFD will run regardless of the remote contact position. b) Manual speed control capability. c) Local/Remote selector switch. In the Remote position, motor speed is determined by the follower signal. In the local position, motor speed is determined by the manual speed control d) Power/On light to indicate that the VFD has tripped on a fault condition. e) Digital meter with selector switch to indicate percent speed and percent load. f) A set of form-C dry contacts, to indicate when the VFD is in the Run mode. g) A set of form-C dry contacts, to indicate when the VFD is in the Fault mode. h) A 0 to 10 V output signal to vary in direct proportion to the controller's speed. i) VFD to have terminal strip and N.C. safety contacts such as freezstats, smoke alarms, etc. VFD to safety shut down in drive or bypass mode when contacts open. | Comply for all points using the VSD Keypad & the built in control card |
| Adjustments will include the following: a) Maximum speed, adjustable 15 to 100 percent base speed. b) Acceleration time, adjustable 3 to 60 seconds. c) Deceleration time, adjustable 3 to 60 seconds with override circuit to prevent nuisance trips if decal time is set too short. d) Current limit, adjustable 0 to 105 percent. e) Overload trip set point. f) Offset and gain to condition the input speed signal. | Comply using the VSD software |
| Service conditions will cover: g) Ambient temperature, 0 to 45 deg C. h) 0 to 85 percent relative humidity, non-condensing. i) Elevation to 1,000 meters without derating. j) AC line voltage variation, -10 to +10 percent of nominal. | g-We will add the derating curves for all the VSD and per each VSD the output current at 45 C . All the stations have an Air condition with Max Ambient temp 35 , So no deration is required . h-Comply using the cabinet heater i-Altitude Up to 1000 m no derating necessary j-Rated voltage Vn 3 AC 380 V -10 % ... 415 V +6 % for TT, TN-C or TN-S |
| Special features will include the following features in the VFD enclosure while maintaining its UL to ETL listing: k) Manual by-pass shall provide all the circuitry necessary to transfer the motor from the VFD to the power line or from the line to the controller. The by-pass circuitry shall be mounted in a separate section of the VFD enclosure. Motor overload protection shall be provided in both drive and by-pass modes. l) A door interlocked, pad lockable drive disconnect switch shall be provided to disconnect power from the VFD only (The disconnect shall be clearly marked as such). m) A motor circuit protector, MCP, shall be provided as a means of disconnecting all power to both the VFD and by-pass circuits as well as providing short circuit and locked rotor protection to the motor while in the by-pass mode. n) The disconnect and by-pass functions may be accomplished via disconnects, contractors and overloads, or with a four position Drive/Off/Line/Test switch with motor starter and by-pass fuses. | k. Option & Not recommended l-ATV680 has a built in disconnect switch with fuses look at the attached ATV680 design concept m-ATV680 has a built in aR fuses to protect against SC , For the CB it will be on the MCC panel that supply the VSD n-Optional and not recommended |
| 2- Required signals for control system |  |
| Inputs and outputs At least, the following standard Inputs and Outputs shall be provided, to be used in interface with the control system: Analogue Inputs: 1 x Programmable current input 0(4) - 20mA Analogue Output: 1 x Programmable analogue outputs 0(4) - 20mA Logic inputs: 6 x Programmable logic Inputs isolated from the mains (One of these inputs could be used for PTC probe) Specific Fault, local, off, remote Safety input one input dedicated to the Power removal safety function Communications The AC drive shall have the capability for internal mounted communication card. The Modbusplus, Profibus DP, DeviceNet protocols shall be the minimum available for combatable with the control system. Operating conditions | ATV680 has a built in I/O as per the attached document ( ATV680 I/O module ) ATV680 Has a built communication protocol as following : Modbus serial Modbus TCP Ethernet I |
| Operating conditions:  Operating ambient Temperature: up to 50 °C  Max. Relative Humidity (IEC 60068-2-3): 5 95 %, without condensation  Max. Corrosion Level of the Cooling Air: IEC 721-3-3, class 3C1. | We added the derating curves for all the VSD and the output current @45 C as mentioned on point g Service conditions will cover: g) Ambient temperature, 0 to 45 deg C. Also we have a cabint heater for the humidity , ATV680 Allowed pollution: Pollution degree IP54 (optional): 3 according to EN 61800-5-1 Chemical / mechanical classification: 3C3 and 3S3 according to EN 60721-3-3 |