## Sheet1
PART 2 - PRODUCTS
2.1 VARIABLE FREQUENCY DRIVE | Clause | Comment | Reason
| A. Furnish complete variable frequency drives as specified herein for the fans and pumps designated to be variable speed. All standards and optional features shall be included within the VFD enclosure, unless otherwise specified. VFD enclosure shall be IP 54 , to IEC 60529 with inlet air filters. Drive shall be mounted on a floor stand | Comply | ATV650 product is designed for Pump & Fan Applications . ATV650 is wall mounted product with IP degree of protection IP55 conforming to IEC 60529 , All data sheets are attached | https://download.schneider-electric.com/files?p_enDocType=Catalog&p_File_Name=Catalog+Altivar+Process+ATV600+variable+speed+drives.pdf&p_Doc_Ref=DIA2ED2140502EN
| B. VFD shall be provided for motor starting and speed control where specified or shown on electrical or mechanical drawings | Comply | ATV650 has a built in control functions to control the motor /pump speed and to control the motor starting such as : Optimized torque mode Constant torque standard Variable torque standard
| C. VFD shall convert three-phase, 50 hertz utility power to adjustable voltage and frequency, three phase power for stepless motor speed control from 10% to 100% of the motor's 50 hertz speed. Input voltage shall be as specified on the drawing schedules. | Comply | [Us] rated supply voltage 380...480 V Supply frequency 50...60 Hz - 5...5 % 380...480 V - 15...10 %
| D. VFD shall include a converter and an inverter section. The converter section shall convert fixed frequency and voltage AC utility power to DC voltage. All VFDs shall include input line reactors or an isolation transformer as required. The inverter section of the VFD shall invert the DC voltage into a quality output waveform, with adjustable voltage and frequency for stepless motor speed control. The VFD shall maintain a constant V/Hz ratio. The VFD and options shall be tested to IEC 60947-4-1. | Comply | Structure of the ATV650 drive is consists of the Converter & DC bus capatictors & Inverter working through IGBT working with PWM with a Embedded low harmonic DC choke technology complying with standard IEC 61000-3-12 for the 380…480 V offer ,
| E. Power line noise shall be limited to a voltage distortion factor and line notch as defined in IEC 61000 as follows: 1. For motors with full load current below 16 A, comply with IEC 61000-3-2, and as a minimum use 6-pulse rectifier with DC buffer. 2. For motors with full load current below 75 A, comply with IEC 61000-3-4], and as a minimum use 6-pulse rectifier with 3% AC line reactor and DC buffer. 3. For motors with full load current exceeding 75 A and up to 450 A, comply with IEC 61000-3-4, and as a minimum use 6-pulse rectifier with 5% AC line reactor and DC buffer. 4. For motors with full load current exceeding 450 A, comply with IEC 61000-3-4, and as a minimum use 12-pulse rectifier with two secondaries galvanic isolating transformer to provide the necessary phase shift and 5% AC line reactor and DC buffer; as an alternative, active front end technique with LCL filter may be used. | Comply | All the range of the ATV650 from 0.75 KW to 90 KW have the built in Embedded low harmonic DC choke technology complying with standard IEC 61000-3-12 for the 380…480 V offer . with THDi y 48% for 80 to 100% load, which is used to maintain an optimum power factor on the most common operating range | Look at the ATV600 Catalogue page 19 . https://download.schneider-electric.com/files?p_enDocType=Catalog&p_File_Name=Catalog+Altivar+Process+ATV600+variable+speed+drives.pdf&p_Doc_Ref=DIA2ED2140502EN
| F.The VFD shall comply with EMC directive and standard IEC 61800-3 category C2 (1st environment), the VFD shall include EMC filter. | Comply | Altivar Process drives have integrated radio interference input filters in accordance with the EMC standard for variable speed electrical power drive “products” IEC/EN 61800-3, edition 2, category C2 or C3 in environment 1 or 2, and to comply with the European EMC (electromagnetic compatibility) directive. look at the ATV600 catalogue page 60
| G. Motor noise as a result of the VFD shall be limited to 3 dB over across the line operation measured at 1 meter from the motor's centerline. | Comply | ATV650 has abuilt in Motor noise reduction function Random frequency modulation helps to prevent any resonance, which may occur at a fixed frequency.
| H. VFD's full load amp rating shall meet or exceed NFPA 70, NEC Table 430-250. | Unknow | ALL of our VSD are complying with IEC standards
| I. Protective Features shall include the following: 1. Individual motor overload protection for each motor controlled. 2. Protection against input power under-voltage (for non-emergency motors only), overvoltage, and phase loss. 3. Protection against output current overload and instantaneous over-current. 4. Protection against over-temperature within the VFD enclosure. 5. Protection against over-voltage on the DC bus.B11 6. Thermistor motor protection relay interface. 7. Protect VFD from sustained power of phase loss. Under-voltage trip activates automatically when line voltage drops more than 10 percent below rated input voltage. 8. Automatically reset faults due to under-voltage, over-voltage, phase loss, or overtemperature. 9. Protection against output short circuit and motor winding shorting to case faults. 10. Status lights or digital display for indication of individual fault conditions. 11. Controller capable of operating without a motor or any other equipment connected to the drive output to facilitate start-up and troubleshooting. 12. Input line reactors shall be provided to minimize harmonics introduced to the AC line and to provide additional protection to AC line transients | Comply | All the required protection functions are available as per the below list available on the data sheet ( attached per each VSD ) Safe torque off: motor Motor phase break: motor Thermal protection: drive Safe torque off: drive Overheating: drive Overcurrent between output phases and earth: drive Overload of output voltage: drive Short-circuit protection: drive Motor phase break: drive Overvoltages on the DC bus: drive Line supply overvoltage: drive Line supply undervoltage: drive Line supply phase loss: drive Overspeed: drive Break on the control circuit: drive Thermal protection: motor | look at the 762 on the programming manual of ATV600 for full Error & warrning codes
| J. Interface Features for the VFD will include: 1. Door mounted Hand/Off/Auto selector switch to start and stop the VFD. In the Auto position, the VFD will start/stop from the controller. In the Hand position, the VFD will run regardless of the remote contact position. 2. Manual speed control capability. 3. Local/Remote selector switch. In the Remote position, motor speed is determined by the follower signal. In the local position, motor speed is determined by the manual speed control. 4. Power/On light to indicate that the VFD has tripped on a fault condition. 5. Digital meter with selector switch to indicate percent speed and percent load. 6. A set of form-C dry contacts, to indicate when the VFD is in the Run mode. 7. A set of form-C dry contacts, to indicate when the VFD is in the Fault mode. 8. A 0 to 10 V output signal to vary in direct proportion to the controller's speed. 9. VFD to have terminal strip and N.C. safety contacts such as freezstats, smoke alarms, etc. VFD to safety shut down in drive or bypass mode when contacts open. | Comply | All the required features are available on the VSD screen & the VSD control card as follow : Number of integrated I/O Analog inputs 3: Configurable as voltage (0...10 V) or current (0-20 mA/4-20 mA), 2 of them including probes (PTC, PT100, PT1000, or KTY84) Digital inputs 6: Voltage 24 V c (positive or negative logic) Analog outputs 2: Configurable as voltage (0...10 V) or current (0-20 mA) Relay outputs 3: 1 with NO/NC contacts and 2 with NO contacts Safety function inputs 2: For safety function STO | Look at the ATV600 Catalogue page 37 for VSD screen & page 10 for I/O module https://download.schneider-electric.com/files?p_enDocType=Catalog&p_File_Name=Catalog+Altivar+Process+ATV600+variable+speed+drives.pdf&p_Doc_Ref=DIA2ED2140502EN
| K. Adjustments will include the following: 1. Maximum speed, adjustable 15 to 100 percent base speed. 2. Acceleration time, adjustable 3 to 60 seconds. 3. Deceleration time, adjustable 3 to 60 seconds with override circuit to prevent nuisance trips if decal time is set too short. 4. Current limit, adjustable 0 to 105 percent. 5. Overload trip set point. 6. Offset and gain to condition the input speed signal. | Comply | 1- High speed range from 0 - 500 HZ 2- Acceleration time 0 - 6000 sec 3- Deceleration time 0 - 6000 sec 4-Current limit 0- 120 % 5- Over load trip from 0 - 200 % of motor power 6- Offset & gain tuining are available | Look at the ATV600 programming manual https://download.schneider-electric.com/files?p_Doc_Ref=EAV64318&p_enDocType=User+guide&p_File_Name=ATV600_Programming_Manual_EN_EAV64318_11.pdf
| L. Service conditions will cover: 1. Ambient temperature, 0 to 50 deg C. 2. 0 to 95 percent relative humidity, non-condensing. 3. Elevation to 1,000 meters without derating. 4. AC line voltage variation, -10 to +10 percent of nominal | Comply | 1- Ambient air temperature for operation 40…50 °C (with derating factor) -15…40 °C (without derating) 2- Relative humidity 5…95 % without condensation 3- Operating altitude 1000...4800 m with current derating 1 % per 100 m<= 1000 m without derating 4- [Us] rated supply voltage 380...480 V | look at each product data sheet for more clarifications
| M. Control interface: VFD shall be equipped with field-bus module for remote control, monitor and display VFD status and alarms and energy usage from the BMS. Coordinate with BMS for the interface protocol to be adapted and provide the necessary adapter modules accordingly | Comply | ATV650 has a buil inCommunication port protocol: Modbus serial Modbus TCP Modbus TCP