## Compliance Sheet
Technical Submittal — Compliance Sheet
Variable Frequency / Speed Drives (VFD / VSD)
Offered part numbers (from Part Lookup): ATV630D22N4/ATV630C25N4
Source Product Datasheets: ATV630D22N4 → Schneider_Electric_ATV630D22N4_Product_Datasheet.pdf; ATV630C25N4 → Schneider_Electric_ATV630C25N4_Product_Datasheet.pdf
PRIMARY ANSWER — Complies?: Yes = complies; No = does not comply; N/A = not applicable. Why / page / source document support the answer.
Clause | Requirement text | Complies? (Yes/No/N/A) | Why (short) | Consultant page | Source Product Datasheet
VFD-001 | Furnish complete variable frequency drives as specified herein for the fans and pumps designated to be variable speed. All standards and optional features shall be included within the VFD enclosure, unless otherwise specified. VFD enclosure shall be IP 54 with inlet air filters. Drive shall be mounted on a floor stand. Drive to be Active front end- low harmonic drive (THD<5 %), unless otherwise specified. | Yes | Standard ATV630 is a Process drive with DC choke; for Active Front End / THDi <5%, propose low-harmonic ATV600/ATV680 solution or add passive/active harmonic mitigation and… Evidence: ATV630D22N4 /… | 9 | ATV630D22N4: Schneider_Electric_ATV630D22N4_Product_Datasheet.pdf ¦ ATV630C25N4: Schneider_Electric_ATV630C25N4_Product_Datasheet.pdf
J.2 | Individual motor overload protection for each motor controlled. | Yes | Comprehensive electronic protections: overcurrent, short-circuit, phase loss, motor overload/underload, over/undervoltage, overtemperature, stall, ground fault, etc. Evidence: ATV630D22N4 /… | 10 | ATV630D22N4: Schneider_Electric_ATV630D22N4_Product_Datasheet.pdf ¦ ATV630C25N4: Schneider_Electric_ATV630C25N4_Product_Datasheet.pdf
J.3 | Protection against input power under-voltage, over-voltage, and phase loss. | Yes | Comprehensive electronic protections: overcurrent, short-circuit, phase loss, motor overload/underload, over/undervoltage, overtemperature, stall, ground fault, etc. Evidence: ATV630D22N4 /… | 10 | ATV630D22N4: Schneider_Electric_ATV630D22N4_Product_Datasheet.pdf ¦ ATV630C25N4: Schneider_Electric_ATV630C25N4_Product_Datasheet.pdf
J.4 | Protection against output current overload and instantaneous over-current. | Yes | Comprehensive electronic protections: overcurrent, short-circuit, phase loss, motor overload/underload, over/undervoltage, overtemperature, stall, ground fault, etc. Evidence: ATV630D22N4 /… | 10 | ATV630D22N4: Schneider_Electric_ATV630D22N4_Product_Datasheet.pdf ¦ ATV630C25N4: Schneider_Electric_ATV630C25N4_Product_Datasheet.pdf
J.5 | Protection against over-temperature within the VFD enclosure. | Yes | Comprehensive electronic protections: overcurrent, short-circuit, phase loss, motor overload/underload, over/undervoltage, overtemperature, stall, ground fault, etc. Evidence: ATV630D22N4 /… | 10 | ATV630D22N4: Schneider_Electric_ATV630D22N4_Product_Datasheet.pdf ¦ ATV630C25N4: Schneider_Electric_ATV630C25N4_Product_Datasheet.pdf